## Slide 1
Lecture No:14
Topic: Gauss-Seidel Method - Power Flow Solution
Course: Power System Analysis
Presented by
Dr M.S.Giridhar
Professor, Department of EEE
Lakireddy Bali Reddy College of Engineering (Autonomous)
Developed by
Jawaharlal Nehru Technological University Kakinada
www.jntuk.edu.in

## Slide 2: Power flow problem
Im
Ii
ith BUS
In
I2
Ik

## Slide 3: Gauss-Seidel Power Flow Solution-Mathematical Formulation

## Slide 4: A one-line diagram for a four-bus system is shown in figure. The line impedances are given in table. Form YBUS by singular transformation (choose Bus – 1 as reference bus), Determine the voltages at the end of first iteration using GS-method?
1
2
3
4
Line (Bus to Bus) | R (p.u.) | X (p.u.) | G (p.u.) | B (p.u.)
1 – 2 | 0.05 | 0.15 | 2 | -6
1 – 3 | 0.1 | 0.3 | 1 | -3
2 – 3 | 0.15 | 0.45 | 0.666 | -2
2 – 4 | 0.1 | 0.3 | 1 | -3
3 – 4 | 0.05 | 0.15 | 2 | -6
Bus No. | Pi | Qi | Vi | Remarks
1 | - | - | 1.04 | Slack
2 | 0.5 | -0.2 | 1.0 | PQ
3 | -1.0 | 0.5 | 1.0 | PQ
4 | 0.3 | -0.1 | 1.0 | PQ
Initial Value

## Slide 6: CASE-I (1-slack bus and all other buses are PQ-buses)
Algorithm for power flow solution:
The slack bus voltage magnitude and angle are assumed, usually V100 p.u. with the load profile known at each bus (i.e PDi and QDi­ are known).
We allocate PGi and QGi to all generating stations. With this step, bus injections (Pi+jQi) are known at all buses other than the slack bus.
Form YBUS using singular transformation method form the selected graph for the given one-line diagram of the power system.
Compute the bus voltages using the iterative voltage equation as

## Slide 7: Iterative steps
Check for the convergence

## Slide 8: Line power Flows
Compute the power flow from the obtained bus voltages in
step-3 and currents from step-5
Compute the line flow from the obtained bus voltages in step-3

## Slide 9: Convergence
Acceleration of Convergence
Convergence in the gauss-seidal method can some times be speeded up by the use of the acceleration factor
Where α is a real number (generally α = 1.6)