## Slide 1
Lecture No:02
Topic: Formation of element node incidence and bus incidence matrices
Course: Power System Analysis
Presented by
Dr M.S.Giridhar
Professor, Department of EEE
Lakireddy Bali Reddy College of Engineering (Autonomous)
Developed by
Jawaharlal Nehru Technological University Kakinada
www.jntuk.edu.in

## Slide 2: POWER SYSTEM NETWORK INCIDANCE MATRICES
ELEMENT-NODE INCIDANCE MATRIX [A]
The incidence of elements to nodes in a connected graph is shown by element-node incidence matrix
aij = 1 if the ith element is incident to and oriented away form jth node.
aij = -1 if the ith element is incident to and oriented towards jth node.
aij = 0 if the ith element is not incident to jth node.

## Slide 3: GRAPH OF A GIVEN POWER SYSTEM NETWORK
7
A
5
4
D
3
2
B
6
1
1
C

## Slide 4
Node Element |  |  |  |  | 
1 | 1 | -1 | 0 | 0 | 0
2 | 1 | 0 | -1 | 0 | 0
3 | 1 | 0 | 0 | 0 | -1
4 | 0 | 0 | 0 | -1 | 1
5 | 0 | 0 | 1 | -1 | 0
6 | 0 | 1 | -1 | 0 | 0
7 | 0 | 0 | 1 | 0 | -1
1
A
B
C
D
Since the sum of elements in a row are zero, the columns of A are linearly dependent. Hence the rank of A < n.
7
A
5
4
D
3
2
B
6
1
1
C

## Slide 5
Topic: Formation of Ybus Matrix by Singular Transformation
Course: Power System Analysis
Presented by
Dr M.S.Giridhar
Professor, Department of EEE
Lakireddy Bali Reddy College of Engineering (Autonomous)
Developed by
Jawaharlal Nehru Technological University Kakinada
www.jntuk.edu.in

## Slide 6
Primitive Network: A set of unconnected elements is defined as a primitive network.
Performance equation is vpq + epq = Zpqipq
Performance equation is ipq + jpq = ypq vpq
Jpq = -ypq epq
Formulation of network matrices by singular transformation
Ypq
p
q
Ep
Eq
ipq + jpq
jpq
vpq = Ep – Eq
Ep
Zpq
p
q
Eq
ipq
vpq = Ep – Eq
epq

## Slide 7: Kirchoff’s current law at ith Bus
Im
Ii
ith BUS
In
I2
Ik

## Slide 8: FORMATION OF BUS ADMITTANCE BY SINGULAR TRANSFORMATION
The bus admittance matrix Ybus can be obtained by using the bus incidence matrix A to relate the variables and parameters of the primitive network to bus quantities of the interconnected network.
i + j = [y] v ------------------------------(1)
multiply both sides by AT
AT i + AT j = AT [y] v
Since the matrix A shows the incidence of elements to buses
AT i = 0 (KCL) -----------------------------(2)
AT j = IBUS (Algebraic sum of source currents) --------------(3)
Substituting eq(2) and eq(3) in eq(1) we have
IBUS = AT [y]v----------------------------------(4)
Power into the network is (I* BUS)T EBUS
Sum of powers into the primitive network is (j*)Tv
Since transformation of variables must be power invariant
(I* BUS)T EBUS = (j*)Tv ---------------------(5)

## Slide 9: FORMATION OF BUS ADMITTANCE BY SINGULAR TRANSFORMATION
Taking the conjugate transpose of eq.(3)
(I* BUS)T = (j*)TA*
A* = A since A is a real matrix
So, (I* BUS)T = (j*)TA ------------------------(6)
Substituting eq.(6) into eq.(5)
(j*)T A EBUS = (j*)Tv
A EBUS = v ----------------------------(7)
Substituting eq.(7) into eq.(4)
IBUS = AT [y] A EBUS
Which is IBUS = YBUS EBUS
So, YBUS = AT [y] A
As the bus incidence matrix A is a singular, therefore YBUS formation is a singular transformation of [y].
The ZBUS can be calculated from YBUS as
ZBUS = Y-1 BUS = (AT [y] A)-1

## Slide 10: Transmission Line - -Model
yik
yi0
Yk0
i
k

## Slide 11
FORMATION OF YBUS MATRIX BY DISRECT INSPECTION