## Slide 1
Topic: Per Unit Quantities–Single line diagram – Impedance diagram of a power system
Course: Power System Analysis
Presented by
Dr M.S.Giridhar
Professor, Department of EEE
Lakireddy Bali Reddy College of Engineering (Autonomous)
Developed by
Jawaharlal Nehru Technological University Kakinada
www.jntuk.edu.in

## Slide 2: Def:- Per unit value of any quantity is the ratio of the actual value in any units to the base value in the same units.
G
M1
M2
a
b
c
d
e
f
Fig:- One-line Diagram of Power System

## Slide 3
Once the base KV and base KVAs is selected in one part of the system. The base values for a three-phase system are understood to be line-to-line KV’s and three-phase KVA’s.
The base KV for one side of the transformer is selected, then the other side base KV can be selected based on transformation ratio.
The base KVA is same in all parts of the system.
Impedance information is given for three-phase transformers by the manufacturer in per unit or percent on the base determined by their own ratings.
Advantages of per unit system of representation

## Slide 4: Advantages of per unit system of representation
The per unit impedances of the machines of the same type and widely different rating usually lie within a narrow range although the ohmic values differ materially for machines of different ratings.
Per-unit impedance once expressed on the proper base is the same referred to either side of the transformer.
The way in which transformers are connected in three-phase circuits does not affect the per-unit impedances of the equivalent circuit although the transformer connection does determine the relation between the voltage bases on the two sides of the transformer.

## Slide 5: Per unit value of any quantity is the ratio of the actual value in any units to the base value in the same units.

## Slide 6: Construction of sequence networks of power system
A 25 MVA, 11 kV 3-phase generator has a sub-transient reactance of 20%. The generators supplies two motors over a transmission line with transformers at both ends as shown in Fig. The motors have rated inputs of 15 and 7.5 MVA, both 10 kV with 25% sub-transient reactance. The 3-phase transformers are both rated 30 MVA, 10.8/121 kV, connection -Y with leakage reactance of 10% each. The series reactance of line is 100 ohms. Draw the positive and negative sequence networks of the system with the reactance marked in per unit.

## Slide 7
G
M1
M2
a
b
c
d
e
f
25 MVA, 11 kV 3-phase generator has a sub-transient reactance of 20%
The motors have rated inputs of 15 and 7.5 MVA, both 10 kV with 25% sub-transient reactance
3-phase transformers rated 30 MVA, 10.8/121 kV, with leakage reactance of 10% .
Series reactance of line is 100 ohms.

## Slide 8: Given power system component Ratings
Choose Base MVA as 25 MVA.
Generator circuit Base kV - 11 kV
Transmission Line Base kV – 11×(121/10.8) = 123.2 kV
Motor circuit Base kV – 123.2×(10.8/121) = 11 kV
Base Values are - NEW Values
Machine Ratings are – OLD Values
P.u (new) = p.u (old) ×(MVA(new)/MVA(old) )×(kV(old)/kV(new))2

## Slide 9: Per unit values
Component | Base values (NEW) | Machine Ratings (OLD) | Per unit Reactance (NEW)
Transformer | 25 MVA, 11kV | 30 MVA, 10.8 kV | 0.1×(25/30) ×(10.8/11)2 = 0.0805
Transmission line | 25 MVA, 123.2 kV |  | (100×25)/(123.2)2 = 0.164
Motor-1 | 25 MVA,11 kV | 15 MVA, 10 kV | 0.25×(25/15) ×(10/11)2 = 0.345
Motor-2 | 25 MVA, 11 kV | 7.5 MVA, 10 kV | 0.25×(25/7.5)×(10/11)2 = 0.69

## Slide 10
Eg
Em2
Em1
j0.2
j0.0805
j0.164
j0.0805
J0.345
J0.69
POSITIVE SEQUENCE REACTANCE DIAGRAM OF THE GIVEN POWER SYSTEM NETWORK

## Slide 11
j0.2
j0.0805
j0.164
j0.0805
j0.345
j0.69
NEGATIVE SEQUENCE REACTANCE DIAGRAM OF THE GIVEN POWER SYSTEM NETWORK